FIRE SAFETY INSPECTION CHECKLIST

# REFERENCE:

Inspection Order No. (IO) :	 Date Issued	:	 Date Inspected	:

- NATURE OF INSPECTION CONDUCTED (Check appropriate box)

  - [ ] Inspection during construction

  - [ ] FSIC for Certificate of Annual Inspection (PEZA)

  - [ ] FSIC for Certificate for Occupancy

  - [ ] FSIC for Business Permit (New/Renewal)

  - [ ] Verification Inspection for Compliance:

[ ] NTC / [ ] NTCV / [ ] Abatement [ ] Closure

  - Others (Specify) :

# REQUIREMENTS

  - [ ] FSIC for Occupancy:

    - Fire Safety Compliance and Commissioning Report (FSCCR) (if applicable)

  - [ ] FSIC for New / Renewal / Annual Inspection / Others:

Yes [  ] / No [  ]

    - Fire Safety Maintenance Report (FSMR) (if applicable)	Yes [  ] / No [  ]

# GENERAL INFORMATION

Name of Building	: 	 Address	: 	 Business Name	: 	 Nature of Business	: 	 Name of owner/Representative : 	 Contact No.	:

| [ ] FSIC for Occupancy: |  |  |  |
| --- | --- | --- | --- |
| - FSEC No. | : | / Date Issued | : |
| - Building Permit | : | / Date Issued | : |
| [ ] FSIC for New / Renewal / Annual Inspection / Others: |  |  |  |
| - FSIC No. (Latest) | : | / Date Issued | : |
| - Certificate of Fire Drill | : | / Date Issued | : |
| - Business Permit No. | : | / Date Issued | : |
| - Fire Insurance Policy No. (If any) | : | / Date Issued | : |

# CONSTRUCTION TYPE

[ ] Type I : Concrete & Steel (Fire Resistive)

[ ] Type II : Concrete & Exposed Steel (Noncombustible)

[ ] Type III : Concrete & Wood (Ordinary)

[ ] Type IV : Heavy Timber (Large mass wood) [ ] Type V : Wood frame (Lightweight wood)

# WALLS / CEILING INTERIOR FINISH

[ ] Class A : Flame spread index, 0–25;smoke developed index, 0–450

[ ] Class B : Flame spread index, 26–75; smoke developed index, 0–450

[ ] Class C : Flame spread index, 76–200; smoke developed index, 0–450 (Note: Flame Spread Index can be seen in the technical specification of the product) FLOOR INTERIOR FINISH

[ ] Class I : Critical radiant flux, not less than 0.45 W/cm2.

[ ] Class II : Critical radiant flux, not more than 0.22 W/cm2, but less than 0.45W/cm2

(Note: Flame Spread Index can be seen in the technical specification of the product)

# SECTIONAL OCCUPANCY (INDICATE SPECIFIC USAGE OF EACH FLOOR, PART OR PORTION OF THE BUILDING)

Basement :

Ground floor:

Second floor:

Third floor :

Fourth Floor:	 Nth Floor	:

Use separate sheet if necessary

GENERAL OCCUPANCY CLASSIFICATION

[ ] Assembly / [ ] Educational / [  ] Day Care / [ ] Health Care

[ ] Detention and Correctional / [ ] Residential / [ ] Residential Board and Care [ ] Mercantile / [ ] Business / [ ] Industrial / [ ] Storage / [ ] Special Structure.

OTHER INFORMATION

Maximum Occupant Load: 		P/Floor	 Number of Stories: 	Storey Building Height	: 	m	Highrise: [ ] Yes / [ ] No

- MEANS OF EGRESS

# EXIT ACCESS

[ ] Doors / [ ] Corridors  / [ ] Hallways / [ ] Passageways / [  ] Anterooms / [ ] Ramps

Horizontal components		Actual Dimensions

Passed	Failed	Remarks / Corrective Action

| Doors : |  | m | [ | ] | [ | ] | : |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Corridors / Hallways : |  | m | [ | ] | [ | ] | : |
| Passageways : |  | m | [ | ] | [ | ] | : |
| Lobby / Anteroom : |  | m | [ | ] | [ | ] | : |
| Ramps : |  | m | [ | ] | [ | ] | : |
| Common path of travel : |  | m | [ | ] | [ | ] | : |
| Dead end : |  | m | [ | ] | [ | ] | : |
| Travel distance : |  | m | [ | ] | [ | ] | : |

|  | Actual Dim. | Passed | Failed |
| --- | --- | --- | --- |
| Any door leaf in a means of egress shall leave not less than one-half of the required width of an aisle, a corridor, a passageway, or a landing unobstructed. |  | [ ] | [ ] |
| Any door leaf in a means of egress shall not project more than 180 mm into the required width of an aisle, a corridor, a passageway, or a landing, unless the door leaf is equipped with an approved self-closing device. |  | [ ] | [ ] |
| At least two (2) means of egress for each room with occupant load ≥ 50 or with hazard content. |  | [ ] | [ ] |
| Each guest door used as means of egress shall at least 20 minutes fire resistant. |  | [ ] | [ ] |
| Doors that open directly onto exit access corridors shall be self-closing and self-latching. |  | [ ] | [ ] |
| There shall no openings in corridor partitions other than door openings. |  | [ ] | [ ] |
| Free from any obstruction. |  | [ ] | [ ] |
| No flammable material stored. |  | [ ] | [ ] |

# EXITS

[ ] Normal Stairs /   [ ] Curved Stairs /  [ ] Spiral Stairs /  [ ] Winding Stairs [ ] Horizontal Exits /  [ ] Outside Stairs / Exit Passageways / Fire Escape Stairs [ ] Fire Escape Ladder (for 1 & 2 family dwelling only)

[ ] Slide Escape (for Industrial Occupancy Only)

Components	Clear Width	Passed	Failed	Remarks / Corrective Action

| Exits Doors | : m | [ | ] | [ | ] |
| --- | --- | --- | --- | --- | --- |
| Normal Stairs | : m | [ | ] | [ | ] |
| Curve stairs | : m | [ | ] | [ | ] |
| Winding Stairs | : m | [ | ] | [ | ] |
| Horizontal Exits | : m | [ | ] | [ | ] |
| Outside Stairs | : m | [ | ] | [ | ] |
| Exit Passageways | : m | [ | ] | [ | ] |
| Fire Escape Stairs | : m | [ | ] | [ | ] |
| Fire Escape Ladders | : m | [ | ] | [ | ] |
| Slide Escape | : m | [ | ] | [ | ] |

:

:

:

:

:

:

:

:

:

:

|  | Actual Dim. | Passed | Failed |
| --- | --- | --- | --- |
| At least two (2) means of egress for each floor. |  | [ ] | [ ] |
| Doors assembly: 60 minutes fire resistant for three (3) communicating level and below. |  | [ ] | [ ] |
| Doors assembly: 90 minutes fire resistant for four (4) communicating level and above. |  | [ ] | [ ] |
| Exits Doors provided with Re-entry mechanism at every four (4) storey. |  | [ ] | [ ] |
| Stair thread: Minimum depth = 280 mm. |  | [ ] | [ ] |
| Stair riser: Minimum / Maximum height = 100 mm / 180 mm. |  | [ ] | [ ] |
| Minimum stair head room: 2000mm |  | [ ] | [ ] |
| Stair provided with Guard and Handrails. |  | [ ] | [ ] |
| Maximum handrails projections: 114 mm. |  | [ ] | [ ] |
| Stair landing shall not be less than the required width of exit door. |  | [ ] | [ ] |
| Exits doors open and close properly |  | [ ] | [ ] |
| Doors swing in direction of egress. |  | [ ] | [ ] |
| Exit Doors provided with panic hardware, vision panel, and self-closing mechanism. |  | [ ] | [ ] |
| There shall be no enclosed usable space under the stairs in an exit enclosure nor shall the open space under such stairs be used for any purpose. |  | [ ] | [ ] |
| Interior finish: Class B |  | [ ] | [ ] |

# EXITS DISCHARGE

|  | Actual Dim. | Passed | Failed |
| --- | --- | --- | --- |
| Remoteness of exit discharge not less than ½ of length of the overall dimension of the building or area to be served. |  | [ ] | [ ] |
| Remoteness of exit discharge not less than 1/3 of length of the overall dimension of the building or area to be served is the bldg. is protected throughout by ASASS. |  | [ ] | [ ] |
| Exterior grounds are kept clear of objects that might impede evacuation or firefighting equipment |  | [ ] | [ ] |
| Terminate directly at a public way or at an exterior exit discharge. |  | [ ] | [ ] |

# SIGNS, LIGHTING, AND EXITS SIGNAGE

- MARKING OF MEANS OF EGRESS (EXIT)

|  | Actual Dim. | Passed | Failed |
| --- | --- | --- | --- |
| Minimum letter height, 150 mm |  | [ ] | [ ] |
| EXIT signs are posted along Exit access, Exits and Exit discharge |  | [ ] | [ ] |
| EXIT signs are properly illuminated |  | [ ] | [ ] |

# MARKING OF MEANS OF EGRESS (EMERGENCY EVACUATION PLAN)

|  | Passed | Failed |  |
| --- | --- | --- | --- |
| Posted on strategic and conspicuous location inside the building | [ ] | [ ] |  |
| Drawn with a photo-luminescent background to be readable in case of power failure. Containing the following basic information below - “You Are Here/ room number/ building” Marking - Fire Exits - Primary Route to Exit (Nearest to the viewer) - Secondary Route to Exit (Second nearest to the viewer) - Fire alarm pull stations and annunciators - Fire extinguishers/ hose cabinets - Emergency Light - First Aid Kits locations (if applicable) - Emergency Call stations (if applicable - Areas of safe refuge (for high-rise building) - Assembly areas instructions - “In Case of Emergency” instructions | [ ] | [ ] |  |

|  | Actual Dim. | Passed | Failed |
| --- | --- | --- | --- |
| Emergency Evacuation Plan: |  |  |  |
| [ ] Size 330.2 mm wide * 215.9 mm height (Floor area < 50 m²) - Room or spaces |  | [ ] | [ ] |
| [ ] Size 609.6 mm wide * 457.2 mm height (Floor area = 50 – 150 m²) - Room or spaces - Building lobbies upon entry. - Elevator lobbies at every floor. - Hallways and corridors. - On every bend/corner Or every 15m interval in the case of long hallway. |  | [ ] | [ ] |
| [ ] Size 609.6 mm wide * 457.2 mm height (Floor area ≥ 151m²) - Room or spaces - Upon entry of the building - Area of assembly or every 25m interval in the case auditorium & gymnasium. |  | [ ] | [ ] |
| Symbols/icons/logos to be used for the marking shall be in accordance with NFPA 170, Standard for Signs and Symbols. |  |  |  |

# ILLUMINATION OF MEANS OF EGRESS

(All Data Below Shall be Referred from Manufacturers Specifications)

|  | Actual Lux/Time | Passed | Failed |
| --- | --- | --- | --- |
| Floors and other walking surfaces: shall be at least 1 ft-candle (10.8 lux), measured at the floor. |  | [ ] | [ ] |
| In assembly occupancies: walking surfaces of exit access shall be at least 0.2 ft-candle (2.2 lux) |  | [ ] | [ ] |
| Stairs: shall be at least 10 ft-candle (108 lux), measured at the walking surfaces. |  | [ ] | [ ] |
| Emergency Lighting |  |  |  |
| [ ] Illumination not less than an average of 1 ft-candle (10.8 lux) and, at any point, not less than 0.1 ft-candle (1.1 lux), measured along the path of egress at floor level. |  | [ ] | [ ] |
| [ ] Emergency lighting system shall be arranged to provide the required illumination automatically in the event of any interruption of normal lighting (e.g. Failure of a public utility, ect..) for a period at least 1.5-hour. |  | [ ] | [ ] |
| [ ] Periodic Testing of Emergency Lighting Equipment (Written record) |  |  |  |

| VII. HAZARD |  |  |  |
| --- | --- | --- | --- |
| Hazard Contents | : | Quantity (Vol. / Weight) | : |
| Hazard Identification Placard | : | Within MAQ | : [ ] Yes / [ ] No |
| Hazard Identification No. | : | Hazard Classification: [ ] Low / [ ] Ordinary / [ | ] High |
| Class | : | Flash Point | : |

Low hazard contents shall be classified as those of such low combustibility that no self-propagating fire therein can occur.

Ordinary hazard contents shall be classified as those that are likely to burn with moderate rapidity or to give off a considerable volume of smoke.

High hazard contents shall be classified as those that are likely to burn with extreme rapidity or from which explosions are likely.

# OTHER FLAMMABLE LIQUIDS (I.E. ALCOHOL, ETHER, ETC…)

|  | Passed | Failed |
| --- | --- | --- |
| Stored in sealed metal containers | [ ] | [ ] |
| Properly dispensed as per SOP | [ ] | [ ] |
| Provided with “NO SMOKING” sign. | [ ] | [ ] |

# MISCELLANEOUS HAZARDS (MECHANICAL EQUIPMENT ROOM, STORAGE, SUPPLY ROOM)

|  | Passed | Failed |
| --- | --- | --- |
| All no smoking areas has adequate signs. | [ ] | [ ] |
| Gasoline/ Diesel is stored in the proper place and in a metal safety can. | [ ] | [ ] |

# HOUSEKEEPING, MAINTENANCE, STORAGE & WASTE DISPOSAL

|  | Passed | Failed |
| --- | --- | --- |
| Brooms, mops, rags and other cleaning supplies stored in metal cabinets or approved cans | [ ] | [ ] |
| Paints, solvents and other flammables stored in metal cabinet: oily rags in metal containers | [ ] | [ ] |
| Dry leaves, shrubbery trimmings and other combustibles kept away from buildings | [ ] | [ ] |

| Automatic Fire Suppression System (Sprinkler) |  |  |  |
| --- | --- | --- | --- |
| Item to Inspect | Procedure How to Inspect | Passed | Failed |
| Sprinkler Pumps | Check automatic start and pressure. | [ ] | [ ] |
| Sprinkler Valves | Valves are locked in the open position, no leaks, corrosion, or other defects noted. | [ ] | [ ] |
| Sprinkler water flow alarm | Open test valve and ensure manual alarm bell functions and sprinkler pumps start. | [ ] | [ ] |
| Wet Standpipe/Fire Hose Cabinet |  |  |  |
| Cabinet Door Operative | Check that door is unobstructed and opens properly. | [ ] | [ ] |
| Hose Condition | Check that hose is not rotted, wet, moldy, etc. | [ ] | [ ] |
| Nozzle | Check that nozzle is in place and operates correctly. | [ ] | [ ] |
| Hose hung properly | Check that hose is hung properly so that it can easily be un-rolled if needed. | [ ] | [ ] |
| Valves and valve handles | Check that valve handles are in place and that valves operate properly and are in the open position. | [ ] | [ ] |
| Fire Pump |  |  |  |
| Pump System | Inspect accuracy of pressure gauges and sensors | [ ] | [ ] |
| Pipings | Check pipings if there is leak | [ ] | [ ] |
| Motor | Check unusual noise or vibrations | [ ] | [ ] |
| Electrical System | Check if there is corrosion in PCBs, cracked cable/wire insulation, leak in plumbing parts, sign of water in electrical part | [ ] | [ ] |
| Fire Detection System |  |  |  |
| Fire Detection System | Random Test of call points and smoke detectors. | [ ] | [ ] |
| Fire Alarm Facilities |  |  |  |
| Location Signs | Check all signs are in place and legible. | [ ] | [ ] |
| Alarm Panels | Check that all alarm panels are functioning correctly and are unobstructed. | [ ] | [ ] |
| Lifts (Elevator) |  |  |  |
| Lifts | All lifts “home” to ground floor during fire test, doors open and lift stops. | [ ] | [ ] |
| Fans | All lift fans operate correctly. | [ ] | [ ] |
| Fireman’s lift | Fireman’s lift can be keyed to operate during fire alarm test. | [ ] | [ ] |

- FIRE PROTECTION A.

B.

C.

| First Aid Fire Protection (Fire Extinguishers) |  |  |  |
| --- | --- | --- | --- |
| Fire Extinguisher Size | Minimal sizes of fire extinguishers for the listed grades of hazards shall be provided on the basis of table 7 & 8 of RIRR of RA 9514. | [ ] | [ ] |
| Minimum number of Extinguisher. | The minimum number of extinguishers shall be sufficient to meet the requirements of table 7 & 8 of RIRR of RA 9514. | [ ] | [ ] |
| Location | All extinguishers are in their proper location. | [ ] | [ ] |
| Seals & Tags | Extinguisher seals and tags are intact and extinguisher was serviced in the last 12 months. | [ ] | [ ] |
| Markings | Proper marking on extinguisher to indicate the type of fire the extinguisher can be used on. | [ ] | [ ] |
| Condition | No leaks, corrosion or other defects noticed. | [ ] | [ ] |
| Pressure | Pressure gauge reads in the “green” area. | [ ] | [ ] |
| Emergency Lighting Systems |  |  |  |
| Battery Lights | All battery powered emergency lighting turns on when mains power is removed | [ ] | [ ] |
| Kitchen |  |  |  |
| Hoods & Vents | Hoods, vents, fans and ducts in good condition and free from grease | [ ] | [ ] |
| Hood Filters | Date of Last Cleaning | [ ] | [ ] |

| BUILDING SERVICE EQUIPMENT |  |  |
| --- | --- | --- |
|  | Passed | Failed |
| Utilities: Cooking equipment protected by AKHFSS (Restaurant and similar establishment with Occupant Load > 50p) | [ ] | [ ] |
| Heating, Ventilating and Air-conditioning: Design & Installation in accordance with PMEC | [ ] | [ ] |
| Smoke Control Systems/Smoke Management shall be provided in the following: [ ] All high-rise buildings (stairwells, at least 1 elevator shaft, zoned smoke control, and vestibule). [ ] Pressurization of smoke refuge area. [ ] Every Atrium of covered mall of over 2- levels / Other type of Occupancy over 3 – levels. [ ] Underground structure and windowless facilities. [ ] All movie houses. [ ] All other buildings or structures with at least 1,115m² single floor area. | [ ] | [ ] |
| Rubbish Chutes, Laundry Chutes, and Flue-Fed Incinerators: (not apply to detached single- or two-family dwelling) [ ] Chutes & Incinerators shall be enclosed. [ ] Design and Maintained in accordance with the latest edition of PMEC. | [ ] | [ ] |

1.

2.

3.

4.

| FIRE WALL (FW) (if required) |  |
| --- | --- |
| Provided with Fire Wall (minimum 2 hours fire resistance) | [ ] Yes / [ ] No |
| FW extension above the roof surface shall not be less than 760mm (See MC No. 2021-064 dated 28 June 2021 for Alternative) | [ ] Yes / [ ] No |
| Wall type: [ ] 125mm Solid Concrete / [ ] 150mm Solid Masonry / [ ] 200mm Hallow Unit Masonry |  |

DEFECTS/DEFICIENCIES

ITEM		 IV:

ITEM V:

# ITEM VI:

# ITEM VII:

# ITEM VIII:

# RECOMMENDATIONS

[ ] Comply the following DEFFECTS/DEFICIENCIES stated above and pay the corresponding Fire Code Fees including the Storage Clearance Fee , Conveyance Clearance Fee before the issuance of Fire Safety Inspection Certificate (FSIC)

[ ] For issuance of	[ ] Notice to Comply

[ ] Notice to Correct Violation [ ] Closure Order

[ ] Abatement Order with Administrative Fine

[ ] Closure Order for the non-payment of Administrative Fine

# ACKNOWLEDGED BY:

Signature Over Printed Name of Owner/ Representative

Fire Safety Inspector/s	Team Leader

Date & Time:

# RECOMMEND APPROVAL:

# CHIEF, FIRE SAFETY ENFORCEMENT SECTION/UNIT

APPROVAL:

CITY/ MUNICIPAL FIRE MARSHAL